## 100 KVA
|  |  | HV | 11000 | 100% | 9200
|  |  | LV | 433 | 50% | 3300
|  |  | LL | 15000 | 15 | Impedance | 5 | 6.25
|  |  | NLL | 1600 | 1.6
|  |  | KVA | 1000
|  |  | Radiator | 1000 X 520 X 17 - 4 Nos
GTP of 1000 KVA 11000/433V transformer |  |  | Tank
|  |  | L | 1100
Sl.NO. | DESCRIPTION |  | W | 435
1 | NAME OF THE MANUFACTURER | General Engineering Works (GEW) | H | 1050
Weight
2 | SERVICE | OUTDOOR CONVERTER DUTY | CCA | 1250
3 | KVA RATING |  | Tank Fitt and Acc | 1950
| HV | COPPER
| LV | COPPER | Oil | 650
4 | RATED VOLTAGE
| HV | 11000 V
| LV | 433 V | R | 1.5
5 | RATED FREQUENCY | 50 Hz | Z | 5
|  |  | X | 4.77
6 | CONNECTIONS
| HV | DELTA | X/R | 3.18
| LV | STAR
7 | NO. OF PHASES | 3 | Regulation at Unity Power factor | 1.61
|  |  | Regulation at 0.8 Unity Power factor | 4.1
8 | CONNECTION SYMBOL | Dyn11
[6 empty] | Load | PF | PF
9 | TAPPINGS - TYPE | On Load Tap Changer | %Eff | 98.37 |  | 1 | 1 | 1
| RANGE | +5% To -15% @ 1.25% |  | 98.68 |  | 0.75 | 1 | 1
| NO. OF STEPS / TAPS | 17/18 |  | 98.94 |  | 0.5 | 1 | 1
| VARIATION ON | HV WINDING
10 | MAX REF. AMBIENT TEMP. IN DEG C | 50 °C
11 | TYPE OF COOLING | ONAN
12 | TEMPERATURE RISE
| TOP OIL | 50 °C
| WINDING | 55 °C
14 | TOTAL LOSSES IN WATTS (IS Tol Applicable)
| No Load Loss | 1600
| Full Load Loss | 15000
15 | % IMPEDANCE @ NORMAL TAP | 5 %
16 | REACTANCE @ RATED VOLTAGE | 4.77 %
17 | NO LOAD CURRENT @ RATED VOLTAGE | ≤3%
18 | INSULATION LEVEL
| P.F. TEST VOLTAGE – HV | 28 KV
| P.F. TEST VOLTAGE – LV | 3 KV
GTP of 1000 KVA 11000/433V transformer
19 | INDUCED OVER VOLTAGE IN kV
| HV | 22 KV
| LV | 0.866 KV
20 | IMPULSE WITHSTAND IN kV PEAK
| FULL WAVE HV | 75
| FULL WAVE LV | -
21 | EFFICIENCY: @ UPF -- %
| @ FULL LOAD: | 98.37
| @ 0.75 FULL LOAD: | 98.68
| @ 0.50 FULL LOAD: | 98.94
22 | REGULATION @ FULL LOAD
| @ UPF --- % | 1.61
| @ 0.8 P F Lag | 4.1
23 | RADIATORS/ FINS MOUNTED ON TANK | YES
24 | NO. OF RADIATORS (subject to change) | 1000 X 520 X 17 - 4 Nos
25 | TERMINAL ARRANGEMENT
| HV | Cable Box
| LV | Flange for Bus Duct (Bus Bar extensions not included)
26 | APPROXIMATE MASS IN kg
| CORE & WINDING | 1250
| TANK FITTINGS & ACC. | 1950
| OIL | 650
| TOTAL | 3850
27 | APPROXIMATE TANK DIMENSIONS :
| LENGTH mm | 1100
| BREADTH mm | 435
| HEIGHT mm | 1050
28 | UNTANKING HEIGHT : | 2100
29 | ACCESSORIES | Buchholz Relay
Radiators with shut-off valve
Explosion Vent
Shut-off Valve
Oil Level Guage
Bi-directional Rollers
OTI and WTI in Marshalling Box
MOG
OSR and PRV for OLTC
GTP of 1000 KVA 11000/433V transformer
30 | Paint Shade | RAL 631 / 7035 OR Please Specify
31 | REFERENCE STANDARDS :
| a) TRANSFORMERS : | IS – 2026
| b) OIL : | IS – 335
| c) BUSHING : | IS – 2099 / 3347 / 8603
| d) LOADING : | IS – 6600